## 6. Purge_Cyl
G/C Valve System
Cylinder Change Purge Sequence
[8 empty] | A | A | A | H | L | H | P | P | P | V
[7 empty] | Acc, | C | G | S | P | P | P | G | G | G | G
|  |  | Alarm | Ack |  | Time | Time | V | C | O | I | V | V | I | V | B | B | Alarm | Alarm
S/No. | Operations | Cycle | Goto | Goto | Message at Controller | (Sec) | (Sec) | [10 empty] | Monitoring | Seq. | Remarks | Alarm Message | bar: P G B
1 | Cylinder Shutoff | 1 | - | 2 | ACV Closed, Press ACK. | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
2 | Process Gas Removal | 10-60 | 1 | - | Process Gas Removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | 7 |  | 7 |  | 7 | bar: V G B
[6 empty] | 13 | 20 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 15 | 35 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 13 | 48 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 50 | [13 empty] | - | 645 |  | 645 |  | 645 | bar: H P I; V G B
[6 empty] | 2 | 52 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: V G B
[6 empty] | 10 | 62 | [10 empty] | SPT & DPT | A | If SPT&DPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 10 |  | 10 |  | 10 | bar: A C V to V G B
3 | Cylinder Shutoff Test | 1 | 1 | - | Cylinder Shutoff Test, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "'Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 7 | 14 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[6 empty] | 2 | 16 | bar: H P I to L P V; V G B
[6 empty] | 2 | 18 | [13 empty] | - | bar: V G B
[6 empty] | 180 | 198 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 198 |  | 198 |  | 198 | bar: A C V to V G B
4 | Close MLPI valve | 1 | - | 5 | Close MLPI Valve , Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | bar: A C V to V G B
5 | Prepurge | 10-60 | 5 | - | Prepurge, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdwon, High Vent Pressure" | bar: V G B
[6 empty] | 13 | 20 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P V; V G B
[6 empty] | 2 | 22 | [13 empty] | - | bar: H P V; V G B
[6 empty] | 2 | 24 | [13 empty] | - | bar: V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: P G V to P G B
[6 empty] | 7 | 33 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: P G I to P G B
[6 empty] | 2 | 35 | [13 empty] | - | bar: P G I to P G B
[6 empty] | 2 | 37 | [13 empty] | - | 74 |  | 370 |  | 2220 | bar: P G V to P G B
6-1 | Cylinder Change | 1 | - | 7 | Change Cylinder; Then press ACK | HLT | HLT | [12 empty] | Touch Key: Ack | bar: A G C; P G I to P G V
6-2 | Cylinder Change (Barcode Option Use) | 1 | - | 7 | Change Cylinder; And Scan Cylinder Barcode | HLT | HLT | [12 empty] | Proceed with sequence if cylinder barcode data is normal | bar: A G C; P G I to P G V
7 | Cylinder Change | 1 |  |  | Change Cylinder; Completed | 2 | 2 | [12 empty] | If Barcode Option Use : PGI, PGV Valve Not Close |  | 2 |  | 2 |  | 2 | bar: A G C; P G I to P G V
9 | Auto Leak Check | 1 | 9 | - | Cylinder Connector Leak Test | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdwon, High Vent Pressure" | bar: A G C; V G B
[6 empty] | 13 | 20 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: A G C; H P V; V G B
[6 empty] | 2 | 22 | [13 empty] | - | bar: A G C; H P V; V G B
[6 empty] | 2 | 24 | [13 empty] | - | bar: A G C; V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: A G C; P G V to P G B
[6 empty] | 7 | 33 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: A G C; P G I to P G B
[6 empty] | 2 | 35 | [13 empty] | - | bar: A G C; P G I to P G B
[6 empty] | 2 | 37 | [13 empty] | - | bar: A G C; P G V to P G B
[5 empty] | (*Stabilizing Time) | 60 | 97 | [10 empty] | SPT | D | If SPT < L/C Pressure S/P, Purge shutdown | "Shutdown, Low Leak Check Pressure" | 194 |  | 970 |  | 5820 | bar: A C V to V G B
[5 empty] | (*User Config set - Leak Check Time) | 60 | 157 | [10 empty] | SPT | D | If ΔSPT > LEAK CHECK TOL', Purge Shutdown | "Shutdown, Auto Leak Check Failure" | 600 |  | 600 |  | 600 | bar: A C V to V G B
10 | Manual Leak Check | 1 | - | 11 | Manual Cyl. Conn. Test; Press Ack | HLT | HLT | [12 empty] | Touch Key: Ack | bar: A G C; P G I to P G B
11 | Manual Leak Check | 1 | - | - | Manual Cyl. Conn. Test Completed | 2 | 2 | [14 empty] | 2 |  | 2 |  | 2 | bar: A G C; P G I to P G B
12 | Post-Purge | 10-60 | 12 | - | Low Side Venting...Wait…(Option) | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[5 empty] | Before Postpurge. | 2 | 9 | bar: L P V; V G B
[6 empty] | 180 | 189 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 2 | 191 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 2 | 193 | [13 empty] | - | 193 |  | 193 |  | 193 | bar: L P V; V G B
[5 empty] | Postpurge, Wait | 7 | 200 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 13 | 213 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P V; V G B
[6 empty] | 2 | 215 | [13 empty] | - | bar: H P V; V G B
[6 empty] | 2 | 217 | [13 empty] | - | bar: V G B
[6 empty] | 2 | 219 | [13 empty] | - | bar: P G V to P G B
[6 empty] | 7 | 226 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: P G I to P G B
[6 empty] | 2 | 228 | [13 empty] | - | bar: P G I to P G B
[6 empty] | 2 | 230 | [13 empty] | - | 74 |  | 370 |  | 2220 | bar: P G V to P G B
13 | Open MLPI Valve | 1 | - | 14 | Open MLPI valve; Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
14 | Post Purge Venting | 1 | - | - | Post Purge Venting | 6 | 6 | [13 empty] | - | bar: H P V; V G B
[6 empty] | 2 | 8 | bar: H P V; V G B
[5 empty] | Post Purge Venting Completed | 2 | 10 | [13 empty] | - | 10 |  | 10 |  | 10 | bar: V G B
15 | Regulator Shutoff Test | 1 | - | 16 | Reg. Shutoff, Close (CCW) Then Press ACK | HLT | HLT | [12 empty] | CCW Reg. Then Touch Key : Ack | - | bar: A C V to V G B
16 | Regulator Shutoff Test | 1 | 16 | - | Reg. Shutoff Test; Wait | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 3 | 10 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 7 | 17 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to H P V; V G B
[6 empty] | 3 | 20 | bar: H P I to H P V; V G B
[6 empty] | 3 | 23 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 3 | 26 | [13 empty] | - | bar: V G B
[6 empty] | 2 | 28 | [13 empty] | - | bar: P G V to P G B
[6 empty] | 13 | 41 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
[6 empty] | 2 | 43 | [13 empty] | - | bar: H P I; P G I to P G B
[6 empty] | 180 | 223 | [10 empty] | DPT | D | If DPT<= 2psig, test pass, else purge shutdown | "Shutdown, Regulator Shutoff Test Failure" | bar: H P I; P G V to P G B
[5 empty] | Reg. Shutoff Test; Completed | 2 | 225 | [13 empty] | - | 225 |  | 225 |  | 225 | bar: H P I
17 | HP, LP side Evacuation | 1 | - | 18 | To Remove Purge Gas, Press ACK | HLT | HLT | [12 empty] | Touch Key : ACK | - | bar: A C V to V G B
18 | HP, LP side Evacuation | 1 | 18 | - | Purge Gas removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [10 empty] | DPT | A | If DPT <= 0 Psig, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: L P V; V G B
[6 empty] | 6 | 19 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 6 | 25 | [12 empty] | Open PGI Valve, When PGV Valve Option is used | bar: H P I to P G I; V G B
[6 empty] | 2 | 27 | [10 empty] | SPT | A | If SPT <= 0 Psig, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to P G I; V G B
[6 empty] | 2 | 29 | bar: H P I; H P V to P G I; V G B
[6 empty] | 2 | 31 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 33 | [13 empty] | - | 33 |  | 33 |  | 33 | bar: V G B
19 | Cylinder Open | 1 | - | 20 | Unlock ACV; Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V
20 | Cylinder Pressure Test | 1 | 20 | - | Cylinder Pressure Test | 30 | 30 | [10 empty] | SPT | A | If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | 30 |  | 30 |  | 30 | bar: A C V
21 | Regulator Adjustment | 1 | 19 | 22 | Adjust Reg. (CW); Then press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
22 | Live Gas Flushing | 1-60 | 22 | - | Close Cylinder Valve, Press ACK | HLT | HLT | bar: A C V; H P I
| (Optionable) |  |  |  | Live Gas Flushing Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 2 | 15 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 7 | 22 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 24 | [11 empty] | A | If Repeat Limit Time <= Run time, Shutdown | "Shutdown, Cylinder Valve not closed" | bar: H P I; V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: V G B
[5 empty] | Open Cylinder Valve, Press ACK | HLT | HLT | [13 empty] | - | bar: A C V
23 | Ready for Service/Standby | 1 | 19 | 24 | Ready for Service/Standby; Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
24 | Ready for Service/Standby | 1 | 19 | 25 | Confirm Service, Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
25 | Service | 1 |  |  | Go Back to Main menu, Press Cancel | 2 | 2 | [14 empty] | 2 |  | 2 |  | 2 | bar: A C V; A S O to H P I
HLT = System halt, waiting for operator's ACK | [21 empty] | 2301 | Sec | 3669 | Sec | 12219 | Sec
[22 empty] | 0.63917 | 38.35 | 1.0192 | 1.15 | 3.3942 | 23.65
[22 empty] | 2 | Cycle | 10 | Cycle | 60 | Cycle
[22 empty] | 0 | hour | 1 | Hour | 3 | Hour
[22 empty] | 38 | min | 1 | Min | 23 | Min
[22 empty] | 21 | sec | 9 | Sec | 39 | Sec
Cycle repeat for user set count
Cycle repeat for user set count
Cycle repeat for user set count
Repeat Until SPT <=0 Psig
Cycle repeat for user set count

## 7. Purge_Man
G/C Valve System
Manifold Maintenance Purge Sequence
[8 empty] | A | A | A | H | L | H | P | P | P | V
[7 empty] | Acc, | C | G | S | P | P | P | G | G | G | G
|  |  | Alarm | Ack |  | Time | Time | V | C | O | I | V | V | I | V | B | B | Alarm | Alarm
S/No. | Operations | Cycle | Goto | Goto | Message at Controller | (Sec) | (Sec) | [10 empty] | Monitoring | Seq. | Remarks | Alarm Message | bar: P G B
1 | Cylinder Shutoff | 1 | - | 2 | ACV Closed, Press ACK. | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
2 | Process Gas Removal | 10-60 | 1 | - | Process Gas Removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | 7 |  | 7 |  | 7 | bar: V G B
[6 empty] | 13 | 20 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 15 | 35 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 13 | 48 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 50 | [13 empty] | - | 645 |  | 645 |  | 645 | bar: H P I; V G B
[6 empty] | 2 | 52 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: V G B
[6 empty] | 10 | 62 | [10 empty] | SPT & DPT | A | If SPT&DPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 10 |  | 10 |  | 10 | bar: A C V to V G B
3 | Cylinder Shutoff Test | 1 | 1 | - | Cylinder Shutoff Test, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "'Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 7 | 14 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[6 empty] | 2 | 16 | bar: H P I to L P V; V G B
[6 empty] | 2 | 18 | [13 empty] | - | bar: V G B
[6 empty] | 180 | 198 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 198 |  | 198 |  | 198 | bar: A C V to V G B
4 | Close MLPI valve | 1 | - | 5 | Close MLPI Valve; Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
5 | Open Reglator | 1 | - | 6 | Open Reg.(CW), Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
6 | Manifold Purge Entry | 10-60 | 6 | - | Manifold purge Entry, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdwon, High Vent Pressure" | bar: H P I; V G B
[6 empty] | 6 | 13 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[6 empty] | 2 | 15 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 2 | 17 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 19 | [13 empty] | - | bar: H P I; P G V to P G B
[6 empty] | 10 | 29 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
[6 empty] | 2 | 31 | [13 empty] | - | bar: H P I; P G I to P G B
[6 empty] | 2 | 33 | [13 empty] | - | 66 |  | 330 |  | 1980 | bar: H P I; P G V to P G B
7 | Manifold Purge Venting | 1 | - | - | Manifold Purge; Venting | 6 | 6 | [13 empty] | - | bar: H P I to L P V
[6 empty] | 2 | 8 | [13 empty] | - | 8 |  | 8 |  | 8 | bar: H P I to L P V
8 | Perform Maintenance | 1 | - | 9 | Maintenance completed, Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
[6 empty] | 2 | 2 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: H P I; P G I to P G V
9 | Auto Leak Check | 1 | 9 | - | Manifold Connector Leak Test | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 13 | 20 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[6 empty] | 2 | 22 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 2 | 24 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: H P I; P G V to P G B
[6 empty] | 7 | 33 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
[6 empty] | 2 | 35 | bar: H P I; P G I to P G B
[6 empty] | 2 | 37 | [13 empty] | - | bar: H P I; P G V to P G B
[5 empty] | (*Stabilizing Time) | 60 | 97 | [10 empty] | SPT | D | If SPT < L/C Pressure S/P, Purge shutdown | "Shutdown, Low Leak Check Pressure" | 194 |  | 970 |  | 5820 | bar: A C V to V G B
[5 empty] | (*User Config set - Leak Check Time) | 60 | 157 | [10 empty] | SPT | D | If ΔSPT > LEAK CHECK TOL', Purge Shutdown | "Shutdown, Auto Leak Check Failure" | 600 |  | 600 |  | 600 | bar: A C V to V G B
10 | Manual Leak Check | 1 | - | 10 | Manual Manifold Conn. Test; Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: H P I; P G I to P G B
11 | Manual Leak Check | 1 | - | - | Manual Leak Check Completed. | 2 | 2 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: H P I; P G I to P G B
12 | Post-Purge | 10-60 | 12 | - | Low Side Venting...Wait…(Option) | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: H P I; V G B
[5 empty] | Before Postpurge. | 180 | 187 | bar: H P I to L P V; V G B
[6 empty] | 2 | 189 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 2 | 191 | [13 empty] | - | 191 |  | 191 |  | 191 | bar: H P I; V G B
[5 empty] | Postpurge | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: H P I; V G B
[5 empty] | To skip post-purge, press Ack; Else wait | 7 | 14 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
| System will HLT for 3 minutes, |  |  |  |  | 2 | 16 | [13 empty] | - | bar: H P I to L P V; V G B
| If no ACK, start Post Purge. |  |  |  |  | 2 | 18 | [13 empty] | - | bar: H P I; V G B
| Message will change ----------------------------------> |  |  |  | Post Purge Entry, Wait… | 2 | 20 | [13 empty] | - | bar: H P I; P G V to P G B
| If ACK is pressed within 3 minutes, |  |  |  |  | 10 | 30 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
| Post Purge will be skip to step13 |  |  |  |  | 2 | 32 | bar: H P I; P G I to P G B
[6 empty] | 2 | 34 | [14 empty] | 68 |  | 340 |  | 2040 | bar: H P I; P G V to P G B
13 | Open MLPI Valve | 1 | - | 14 | Open MLPI Valve, Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
14 | Post Purge venting | 1 | 14 | - | Post Purge Venting | 2 | 2 | bar: H P I; V G B
[6 empty] | 60 | 62 | bar: H P I to L P V; V G B
[6 empty] | 2 | 64 | [10 empty] | SPT & DPT | A | If SPT& DPT<= 0 Psig, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[5 empty] | Post Purge Venting Completed | 2 | 66 | [13 empty] | - | 66 |  | 66 |  | 66 | bar: H P I; V G B
15 | Regulator Shutoff Test | 1 | - | 16 | Reg. Shutoff, Close (CCW) Then Press ACK | HLT | HLT | [12 empty] | CCW Reg. Then Touch Key : Ack | - | bar: A C V to V G B
16 | Regulator Shutoff Test | 1 | 16 | - | Reg. Shutoff Test; Wait | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 3 | 10 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 7 | 17 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to H P V; V G B
[6 empty] | 3 | 20 | bar: H P I to H P V; V G B
[6 empty] | 3 | 23 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 3 | 26 | [13 empty] | - | bar: V G B
[6 empty] | 2 | 28 | [13 empty] | - | bar: P G V to P G B
[6 empty] | 13 | 41 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
[6 empty] | 2 | 43 | [13 empty] | - | bar: H P I; P G I to P G B
[6 empty] | 180 | 223 | [10 empty] | DPT | D | If DPT<= 2psig, test pass, else purge shutdown | "Shutdown, Regulator Shutoff Test Failure" | bar: H P I; P G V to P G B
[5 empty] | Reg. Shutoff Test; Completed | 2 | 225 | [13 empty] | - | 225 |  | 225 |  | 225 | bar: H P I
17 | HP, LP side Evacuation | 1 | - | 18 | To Remove Purge Gas, Press ACK | HLT | HLT | [12 empty] | Touch Key : ACK | - | bar: A C V to V G B
18 | HP, LP side Evacuation | 1 | 18 | - | Purge Gas removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [10 empty] | DPT | A | If DPT <= 0 Psi, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: L P V; V G B
[6 empty] | 6 | 19 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 6 | 25 | [12 empty] | Open PGI Valve, When PGV Valve Option is used | bar: H P I to P G I; V G B
[6 empty] | 2 | 27 | [10 empty] | SPT | A | If SPT <= 0 Psi, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to P G I; V G B
[6 empty] | 2 | 29 | bar: H P I; H P V to P G I; V G B
[6 empty] | 2 | 31 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 33 | [13 empty] | - | 33 |  | 33 |  | 33 | bar: V G B
19 | Cylinder Open | 1 | - | 20 | Unlock ACV; Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V
20 | Cylinder Pressure Test | 1 | 20 | - | Cylinder Pressure Test | 30 | 30 | [10 empty] | SPT | A | If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | 30 |  | 30 |  | 30 | bar: A C V
21 | Regulator Adjustment | 1 | 20 | 22 | Adjust Reg. (CW); Then press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
22 | Live Gas Flushing | 1-60 | 22 | - | Close Cylinder Valve, Press ACK | HLT | HLT | bar: A C V; H P I
| (Optionable) |  |  |  | Live Gas Flushing Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 2 | 15 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 7 | 22 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 24 | [11 empty] | A | If Repeat Limit Time <= Run time, Shutdown | "Shutdown, Cylinder Valve not closed" | bar: H P I; V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: V G B
[5 empty] | Open Cylinder Valve, Press ACK | HLT | HLT | [13 empty] | - | bar: A C V
23 | Ready for Service/Standby | 1 | 20 | 24 | Ready for Service/Standby; Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
24 | Ready for Service/Standby | 1 | 20 | 25 | Confirm Service, Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
25 | Service | 1 |  |  | Go Back to Main menu, Press Cancel | 2 | 2 | [14 empty] | 2 |  | 2 |  | 2 | bar: A C V; A S O to H P I
HLT = System halt, waiting for operator's ACK | [21 empty] | 2342 | Sec | 3654 | Sec | 11854
[22 empty] | 0.65056 | 39.0333 | 1.015 | 0.9 | 3.2928 | 17.5667
[22 empty] | 2 | Cycle | 10 | Cycle | 60 | Cycle
[22 empty] | 0 | hour | 1 | Hour | 3 | Hour
[22 empty] | 39 | min | 0 | Min | 17 | Min
[22 empty] | 2 | sec | 54 | Sec | 34 | Sec
Cycle repeat for user set count
Cycle repeat for user set count
Cycle repeat for user set count
Repeat Until SPT <=0 Psig
Cycle repeat for user set count

## 8. Purge_line
G/C Valve System
Line Maintenance Purge Sequence
[8 empty] | A | A | A | H | L | H | P | P | P | V
[7 empty] | Acc, | C | G | S | P | P | P | G | G | G | G
|  |  | Alarm | Ack |  | Time | Time | V | C | O | I | V | V | I | V | B | B | Alarm | Alarm
S/No. | Operations | Cycle | Goto | Goto | Message at Controller | (Sec) | (Sec) | [10 empty] | Monitoring | Seq. | Remarks | Alarm Message | bar: P G B
1 | Cylinder Shutoff | 1 | - | 2 | ACV Closed, Press ACK. | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
2 | Process Gas Removal | 10-60 | 1 | - | Process Gas Removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | 7 |  | 7 |  | 7 | bar: V G B
[6 empty] | 13 | 20 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 15 | 35 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 13 | 48 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 50 | [13 empty] | - | 645 |  | 645 |  | 645 | bar: H P I; V G B
[6 empty] | 2 | 52 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: V G B
[6 empty] | 10 | 62 | [10 empty] | SPT & DPT | A | If SPT&DPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 10 |  | 10 |  | 10 | bar: A C V to V G B
3 | Cylinder Shutoff Test | 1 | 1 | - | Cylinder Shutoff Test, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "'Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 7 | 14 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to L P V; V G B
[6 empty] | 2 | 16 | bar: H P I to L P V; V G B
[6 empty] | 2 | 18 | [13 empty] | - | bar: V G B
[6 empty] | 180 | 198 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | 198 |  | 198 |  | 198 | bar: A C V to V G B
4 | Open MLPI valve | 1 | - | 5 | Open MLPI Valve, Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
5 | Open Regulator | 1 | - | 6 | Open Reg.(CW), Then Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
6 | Line Purge Entry | 10-60 | 6 | - | Line Purge Entry, Wait | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: A S O to H P I; V G B
[6 empty] | 180 | 187 | [10 empty] | SPT | A | If SPT <=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: A S O to L P V; V G B
[6 empty] | 2 | 189 | [13 empty] | - | bar: A S O to L P V; V G B
[6 empty] | 2 | 191 | [13 empty] | - | bar: A S O to H P I; V G B
[6 empty] | 2 | 193 | [13 empty] | - | bar: A S O to H P I; P G V to P G B
[6 empty] | 180 | 373 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: A S O to H P I; P G I to P G B
[6 empty] | 2 | 375 | bar: A S O to H P I; P G I to P G B
[6 empty] | 2 | 377 | [14 empty] | 754 |  | 3770 |  | 22620 | bar: A S O to H P I; P G V to P G B
7 | Line Purge Venting | 1 | - | - | Line Purge; Venting | 180 | 180 | [13 empty] | - | bar: A S O to L P V
[6 empty] | 2 | 182 | [13 empty] | - | 182 |  | 182 |  | 182 | bar: A S O to L P V
8 | Line Maintenance | 1 | - | 9 | Line Maintenance Completed; Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V to V G B
[6 empty] | 2 | 2 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: A S O to H P I; P G I to P G V
9 | Auto Leak Check | 1 | 9 | - | Line Connector Leak Test | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 180 | 187 | [10 empty] | SPT | A | If SPT <=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: A S O to L P V; V G B
[6 empty] | 2 | 189 | [13 empty] | - | bar: A S O to L P V; V G B
[6 empty] | 2 | 191 | [13 empty] | - | bar: A S O to H P I; V G B
[6 empty] | 2 | 193 | [13 empty] | - | bar: A S O to H P I; P G V to P G B
[6 empty] | 180 | 373 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: A S O to H P I; P G I to P G B
[6 empty] | 2 | 195 | [13 empty] | - | bar: A S O to H P I; P G I to P G B
[6 empty] | 2 | 375 | [13 empty] | - | bar: A S O to H P I; P G V to P G B
[5 empty] | (*Stabilizing Time) | 180 | 555 | [10 empty] | SPT | D | If SPT < L/C Pressure S/P, Purge shutdown | "Shutdown, Low Leak Check Pressure" | 1114 |  | 5570 |  | 33420 | bar: A C V to V G B
[5 empty] | (*User Config set - Leak Check Time) | 60 | 615 | [10 empty] | SPT | D | If ΔSPT > LEAK CHECK TOL', Purge Shutdown | "Shutdown, Auto Leak Check Failure" | 600 |  | 600 |  | 600 | bar: A C V to V G B
10 | Manual Leak Check | 1 | - | 11 | Manual Line Conn.Test; Press Ack | HLT | HLT | [13 empty] | - | bar: A S O to H P I; P G I to P G B
11 | Manual Leak Check | 1 | - | - | Manual Leak Check Completed. | 2 | 2 | [13 empty] | - | 2 |  | 2 |  | 2 | bar: A S O to H P I; P G I to P G B
12 | Post-Purge | 10-60 | 12 | - | Low Side Venting...Wait…(Option) | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: A S O to H P I; V G B
[5 empty] | Before Postpurge. | 180 | 187 | bar: A S O to L P V; V G B
[6 empty] | 2 | 189 | [13 empty] | - | bar: A S O to L P V; V G B
[6 empty] | 2 | 191 | [13 empty] | - | 191 |  | 191 |  | 191 | bar: A S O to H P I; V G B
[5 empty] | Postpurge | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: A S O to H P I; V G B
[5 empty] | To skip post-purge, Press Ack; Else wait | 180 | 187 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: A S O to L P V; V G B
| System will HLT for 3 minutes, |  |  |  |  | 2 | 189 | [13 empty] | - | bar: A S O to L P V; V G B
| If no ACK, start Post Purge. |  |  |  |  | 2 | 191 | [13 empty] | - | bar: A S O to H P I; V G B
| Message will change ----------------------------------> |  |  |  | Post Purge Entry, Wait… | 2 | 193 | [13 empty] | - | bar: A S O to H P I; P G V to P G B
| If ACK is pressed within 3 minutes, |  |  |  |  | 180 | 373 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: A S O to H P I; P G I to P G B
| Post Purge will be skip to step13 |  |  |  |  | 2 | 375 | bar: A S O to H P I; P G I to P G B
[6 empty] | 2 | 377 | [14 empty] | 754 |  | 3770 |  | 22620 | bar: A S O to H P I; P G V to P G B
13 | Post Purge venting | 1 | 13 | - | Post Purge Venting | 2 | 2 | [13 empty] | - | bar: A S O to H P I; V G B
[6 empty] | 240 | 242 | bar: A S O to L P V; V G B
[6 empty] | 2 | 244 | [10 empty] | SPT & DPT | A | If SPT& DPT<= 0 Psig, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: A S O to L P V; V G B
[5 empty] | Post Purge Venting Completed | 2 | 246 | [13 empty] | - | 246 |  | 246 |  | 246 | bar: A S O to H P I; V G B
14 | Regulator Shutoff Test | 1 | - | 15 | Reg. Shutoff, Close (CCW) Then Press ACK | HLT | HLT | [12 empty] | CCW Reg. Then Touch Key : Ack | - | bar: A C V to V G B
15 | Regulator Shutoff Test | 1 | 15 | - | Reg. Shutoff Test; Wait | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 3 | 10 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 7 | 17 | [10 empty] | SPT | A | If SPT<=Vacuum Limits, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to H P V; V G B
[6 empty] | 3 | 20 | bar: H P I to H P V; V G B
[6 empty] | 3 | 23 | [13 empty] | - | bar: L P V to H P V; V G B
[6 empty] | 3 | 26 | [13 empty] | - | bar: V G B
[6 empty] | 2 | 28 | [13 empty] | - | bar: P G V to P G B
[6 empty] | 13 | 41 | [10 empty] | PPS & SPT | D | If PPS detected or SPT < Low Purge Pressure, Purge shutdown | "Shutdown, Low Purge Pressure" | bar: H P I; P G I to P G B
[6 empty] | 2 | 43 | [13 empty] | - | bar: H P I; P G I to P G B
[6 empty] | 180 | 223 | [10 empty] | DPT | D | If DPT<= 2psig, test pass, else purge shutdown | "Shutdown, Regulator Shutoff Test Failure" | bar: H P I; P G V to P G B
[5 empty] | Reg. Shutoff Test; Completed | 2 | 225 | [13 empty] | - | 225 |  | 225 |  | 225 | bar: H P I
16 | HP, LP side Evacuation | 1 | - | 17 | To Remove Purge Gas, Press ACK | HLT | HLT | [12 empty] | Touch Key : ACK | - | bar: A C V to V G B
17 | HP, LP side Evacuation | 1 | 17 | - | Purge Gas removal, Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [10 empty] | DPT | A | If DPT <= 0 Psi, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: L P V; V G B
[6 empty] | 6 | 19 | [13 empty] | - | bar: H P I to L P V; V G B
[6 empty] | 6 | 25 | [12 empty] | Open PGI Valve, When PGV Valve Option is used | bar: H P I to P G I; V G B
[6 empty] | 2 | 27 | [10 empty] | SPT | A | If SPT <= 0 Psi, test pass, else purge shutdown | "Shutdown, High Manifold Pressure" | bar: H P I to P G I; V G B
[6 empty] | 2 | 29 | bar: H P I; H P V to P G I; V G B
[6 empty] | 2 | 31 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 33 | [13 empty] | - | 33 |  | 33 |  | 33 | bar: V G B
18 | Cylinder Open | 1 | - | 19 | Unlock ACV; Press ACK | HLT | HLT | [12 empty] | Touch Key : Ack | - | bar: A C V
19 | Cylinder Pressure Test | 1 | 19 | - | Cylinder Pressure Test | 30 | 30 | [10 empty] | SPT | A | If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | 30 |  | 30 |  | 30 | bar: A C V
20 | Regulator Adjustment | 1 | 19 | 21 | Adjust Reg. (CW); Then press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
21 | Live Gas Flushing | 1-60 | 21 | - | Close Cylinder Valve, Press ACK | HLT | HLT | bar: A C V; H P I
| (Optionable) |  |  |  | Live Gas Flushing Wait… | 7 | 7 | [10 empty] | VPS | A | High Vent Check | "Shutdown, High Vent Pressure" | bar: V G B
[6 empty] | 6 | 13 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 2 | 15 | [13 empty] | - | bar: L P V; V G B
[6 empty] | 7 | 22 | [13 empty] | - | bar: H P I; V G B
[6 empty] | 2 | 24 | [11 empty] | A | If Repeat Limit Time <= Run time, Shutdown | "Shutdown, Cylinder Valve not closed" | bar: H P I; V G B
[6 empty] | 2 | 26 | [13 empty] | - | bar: V G B
[5 empty] | Open Cylinder Valve, Press ACK | HLT | HLT | [13 empty] | - | bar: A C V
22 | Ready for Service/Standby | 1 | 19 | 23 | Ready for Service/Standby; Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
23 | Ready for Service/Standby | 1 | 19 | 24 | Confirm Service, Press ACK | HLT | HLT | [10 empty] | SPT | D | Touch Key : Ack, If SPT>= low SPT ; test pass, else shutdown | "Shutdown, Cyl Pressure Test Fail" | bar: A C V; H P I
24 | Service | 1 |  |  | Go Back to Main menu, Press Cancel | 2 | 2 | bar: A C V; A S O to H P I
HLT = System halt, waiting for operator's ACK | [21 empty] | 0 |  | 0 |  | 0
[22 empty] | 4988 | Sec | 15476 | Sec | 81026
[22 empty] | 1.3856 | 23.1333 | 4.2989 | 17.9333 | 22.5072 | 30.4333
[22 empty] | 2 | Cycle | 10 | Cycle | 60 | Cycle
[22 empty] | 1 | hour | 4 | Hour | 22 | Hour
[22 empty] | 23 | min | 17 | Min | 30 | Min
[22 empty] | 8 | sec | 56 | Sec | 26 | Sec
Cycle repeat for user set count
Cycle repeat for user set count
Cycle repeat for user set count
Repeat Until SPT <=0 Psig
Cycle repeat for user set count